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	K O Z L O D U Y  N P P  E A D

	
	Kozloduy 3321, Bulgaria, Tel.: +359 (973) 73530, Fax: +359 (973) 76027




INFORMATION NOTICE


Re: Market consultation pursuant to Article 44 of the PPA for the submission of indicative proposals for ‘Supply of a system for eddy current testing, ultrasonic inspection, and the installation and removal of mechanical plugs on the heat exchanging tubes of ПГВ-1000М-type steam generators’

Dear Sir or Madam,
In connection with the questions received, Kozloduy NPP EAD extends the deadline for calls for indicative proposals until 09 October 2026 and makes the following clarifications:

I. Question:
	A fully dimensioned technical drawing of the steam generator, including all relevant dimensions and distances from the steam generator collector flange in the corresponding cross-section has to be provided, with the welds requiring inspection clearly identified.

I. Answer:
The distance between the welded connection and the flange is about 1600 mm.

II. Question:
Based on the provided technical drawing, the minimum and maximum positioning of the phased-array probes required for the UT examination will be determined.

II. 	Answer:
There is no requirement in the Terms of Reference for the probes to be phased-array probes.

III. Question:
The weld dimensions are required for determining the scope of the heat affected zone (HAZ). The cladding thickness and the root configuration are also of particular importance for defining the inspection parameters and ensuring adequate ultrasonic coverage.

III. Answer:
The total thickness of the welded connection is about 90 mm and the cladding is about 9 mm.

IV. Question:
Particular attention should be given to the ‘hot leg’ side, including the maximum available distances. This information is essential for the design and positioning of the protective umbrella, allowing us to comply with the applicable requirements and to ensure the integrity and the FME zone during the inspection. Accordingly, we would also kindly ask you to provide information regarding the applicable standard under which the UT examination is required, as well as the applicable acceptance criteria for the evaluation of the inspection results.

IV. Answer:
Ultrasonic testing is performed according to ГОСТ 50.05.02-2022.
Evaluation is performed according to НП-084-15.

V.  Question:
Technical documentation shall be provided.

V. 	Answer:
Kozloduy NPP EAD calls for market consultations in order to prepare for the award of a public procurement and to determine an estimated value. A detailed drawing of the steam generator and the welded connections for testing will be provided after signing a Performance Contract and a Declaration of Confidentiality.

Kozloduy NPP EAD informs all potential contractors that the market consultations are conducted on the grounds of Article 44 of the PPA. In this regard, any questions that may arise during the preparation of the indicative proposal shall be sent, within the specified deadlines, to: commercial@npp.bg. 

All the information exchanged during the market consultations will be published in the Buyer’s profile.

Contractors can send their presentations by submitting a request to the email published on the Company’s website.
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